## AMP100
APPENDIX III: MANUFACTURERS' MINIMUM MAINTENANCE REQUIREMENTS
Manufacturers' documentation included in the task lists in Appendix III may be sourced at the following website link:
https://files.barryisett.com/public/folder/2cJfMxYhWEWJXmz_s7qMgQ/AHA%20PM%20Procurement
AMP 100: CENTRAL PARK
Location: | Maintenance Room | Manufacturer | Bock
Equipment: | Domestic Oil Water Heater #1, #2, and #3 | Model No. | 72E
|  | Inspection Dates | Fall and Spring
Maintenance Requirement Check List
1 | Check fuel supply
2 | Check electrical fuses and wiring
3 | Check the electrode assembly; clean and readjust
4 | Check couplings
5 | Check operation of thermostat
6 | Brush and vacuum med heat exchanger
7 | Bleed the pump
8 | Drain tank
9 | Remove hand hole cover; search for lime build up. Remove lime from tank if it exisits.
10 | Check all valves are operational
11 | Check vent system for cracks or blockage
12 | Check oil filter cartridge and oil filter gasket. Replace as needed.
Location: | Rooftop 4th floor (West) | Manufacturer | AAON, inc.
| Rooftop 5th floor (East) | Model No. | RM-A04-8-0-BA01-13A
Equipment: | Heat/Ventilation System | Inspection Dates | Fall and Spring
Maintenance Requirement Check List
1 | Inspect compressor externally
2 | Inspect drive belt; replace as needed
3 | Check lubrication in bearings (If required re-lubricate)
4 | Inspect and clean blowers, air registers, and dampers
5 | Furnish and replace air filter; wash permanent filters
6 | Clean evapotator coils
7 | Check refrigerant charge; recharge up to 10 lbs. as needed
8 | Check condensate drain for blockage.
9 | Check operation of the thermostat
10 | Check fuses, contacts, and heat banks.
11 | Check operation of all limit and safety controls
12 | Check vibration levels
13 | Check and record operating pressures
14 | Check and record motor voltage and amperage
15 | Check blower is free of dust and debris
16 | Check supply and return for debris blockage. Clean if required.
17 | Inspect integrity of exterior duct

## AMP 200
AMP 200: TOWERS EAST
Location: | Basement Mechanical Room | Manufacturer | Weben-Jarco
Equipment: | Domestic Gas Water Heater | Model No. | AJHWB-120 NG
|  | Inspection Dates | Fall and Spring
Maintenance Requirement Check List
1 | Check water system
2 | Check expansion tanks
3 | Check water heater relief valve
4 | Check ignition ground wiring
5 | Check water heater wiring
6 | Check control wiring
7 | Check pressure/temperature gauge
8 | Measure and record amperage and temperature inlet/outlet
9 | Check vent piping
10 | Check air piping
11 | Check water and gas piping for leaks
12 | Check relief valves
13 | Clean heat exchanger
14 | Inspect ignition and flame sense electrodes: replace as needed
15 | Check flame signal
16 | Clean strainers as required.
Location: | Basement Mechanical Room | Manufacturer | Lochinvar
Equipment: | Domestic Gas Water Heater | Model No. | AWN1000
|  | Inspection Dates | Fall and Spring
Maintenance Requirment Check List
1 | Check water system
2 | Check expansion tanks
3 | Check water heater relief valve
4 | Check ignition ground wiring
5 | Check water heater wiring
6 | Check control wiring
7 | Check pressure/temperature gauge
8 | Check vent piping
9 | Check air piping
10 | Check water and gas piping for leaks
11 | Check relief valves and test safety valves
12 | Check operation of all limit and safety controls.
13 | Check modulating motor operation
14 | Check programmer operation
15 | Check and record amp draw on pump motors.
16 | Clean heat exchanger
17 | Inspect ignition and flame sense electrodes: replace as needed.
18 | Check flame signal
19 | Clean strainers as required.
Location: | First Floor Community Room (Storage Closet) | Manufacturer | Trane
Equipment: | A/C Evaporator | Model No. | Climate Changer Type L-10
|  | Inspection Dates | Spring
Maintenance Requirement Check List
1 | Furnish and replace air filter; wash permanent filters
2 | Check refrigerant charge; recharge up to 10 lbs
3 | Check expansion valve operation
4 | Clean and inspect blower assembly
5 | Replace drive belt as needed
6 | Check vibration levels
7 | Check and record operating pressures
8 | Lubricate blower and motor bearings
9 | Check and record super heat temperature
10 | Clean debris from coils.
11 | Check drain pan.
12 | Replace tape around coil access panel when complete.
13 | Inspect integrity of exterior ductwork
AMP 200: TOWERS EAST
Location: | Rear Loading Dock (Outside Cafeteria) | Manufacturer | Carrier
Equipment: | A/C Condenser | Model No. | 38AKS014521
|  | Inspection Dates | Spring
Maintenance Requirement Check List
1 | Clean and lubricate fan assembly
2 | Clean surface debris and dirt in the unit.
3 | Clean all coils
4 | Inspect the coil fins
5 | Inspect all limit and safety controls
6 | Check vibration levels
7 | Check and record operating pressures
Location: | Rooftop (Public Hallways) | Manufacturer | Valent Air Management System
Equipment: | Outdoor Air Packaged RTU | Model No. | VPR-310-40C-80J-C-3CX
|  | Inspection Dates | Fall and Spring
Maintenance Requirement Check List
1 | Clean cooling coils
2 | Clean the drain pan
3 | Review damper operations
4 | Clean air register, blower, and dampers
5 | Clean and adjust ignition pilot assembly
6 | Clear exterior casing
7 | Tighten fan wheels
8 | Clean dirt from the wheel
9 | Check rubber isolators for deterioration
10 | Clean heat exchanger
11 | Verify water pressure
12 | Change the filters
13 | Change belt as needed
14 | Check all limit and safety controls
15 | Check thermostat operation
16 | Check all sensors (clean or replace as needed)
17 | Check all duct connections
18 | Check all gas connections for leaks
19 | Check all strainers; clean as needed.
20 | Check all pumps

## AMP300
AMP 300: GROSS TOWERS
Location: | Construction and Development (Lower Level) | Manufacturer | Trane
Equipment: | A/C Evaporator | Model No. | TWE090A300EL
|  | Inspection Dates | Fall and Spring
Maintenance Requirement Check List
1 | Clean debris from coils.
2 | Check drain pan.
3 | Furnish and replace air filter; wash permanent filters
4 | Replace drive belt as needed
5 | Clean air register, blower, and dampers
6 | Check refrigerant charge; recharge up to 10 lbs
7 | Check expansion valve operation
8 | Check operation of all limits and safety controls
9 | Check vibration levels
10 | Check and record amps and voltage of motors
11 | Check operation of thermostat
12 | Inspect integrity of exterior duct
13 | Replace tape around coil access panel when complete.
Location: | Room 109 LL | Manufacturer | Trane
Equipment: | A/C Condenser | Model No. | TTA090A300FA
|  | Inspection Dates | Fall and Spring
Maintenance Requirement Check List
1 | Clean and lubricate fan assembly
2 | Clean surface debris and dirt in the unit.
3 | Clean all coils.
4 | Inspect the coil fins
5 | Check refrigerant charge; recharge up to 10 lbs
6 | Check expansion valve operation
7 | Check operation of all limits and safety controls
8 | Check vibration levels
9 | Check and record operating pressures
10 | Inspect compressor and associated tubing for damage.
Location: | Boiler Room | Manufacturer | Lochinvar
Equipment: | Domestic Gas Water Boiler #1 and #2 | Model No. | AWN601PM
|  | Inspection Dates | Fall and Spring
Maintenance Requirement Check List
1 | Check water system
2 | Check expansion tanks
3 | Check water heater relief valve
4 | Check ignition ground wiring
5 | Check water heater wiring
6 | Check control wiring
7 | Check pressure/tempature gauge
8 | Check vent piping
9 | Check air piping
10 | Check water and gas piping for leaks
11 | Check relief valves.
12 | Clean heat exchanger
13 | Inspect Ignition and flame sense electrodes; replace as needed
14 | Check flame signal
15 | Clean strainers
AMP 300: GROSS TOWERS
Location: | Cafeteria Loading Dock | Manufacturer | Trane
Equipment: | A/C Condenser | Model No. | CCRAB751CC04AU
|  | Inspection Dates | Spring
Maintenance Requirement Check List
1 | Clean and lubricate fan assembly
2 | Clean surface debris and dirt in the unit
3 | Clean all coils
4 | Inspect the coil fins
5 | Check refrigerant charge; recharge up to 10 lbs
6 | Check expansion valve operation
7 | Check operation of all limits and safety controls
8 | Check vibration levels
9 | Check and record operating pressures
10 | Check and record voltage and amps of motors
11 | Inspect compressor and associated tubing for damage
Location: | Cafeteria Fire Pump Room | Manufacturer | Trane
Equipment: | A/C Evaporator | Model No. | SCRBB7565P01011
|  | Inspection Dates | Spring
Maintenance Requirement Check List
1 | Clean debris from coils.
2 | Check drain pan.
3 | Lubricate blower and motor bearings
4 | Furnish and replace air filter; wash permanent filters
5 | Replace drive belt as needed
6 | Clean air register, blower, and dampers
7 | Check refrigerant charge; recharge up to 10 lbs
8 | Check expansion valve operation
9 | Check and record operating pressures
10 | Check and record voltage and amps of motors
11 | Check vibration levels
12 | Check operation of all limits and safety controls
13 | Check operation of thermostat
14 | Inspect integrity of exterior duct
15 | Replace tape around coil access panel when complete.
Location: | Public Hallways (Floors 2-8) | Manufacturer | McQuay International
Equipment: | Heat/Ventilation | Model No. | UAEQ5054KG12H
|  | Inspection Dates | Mar/Jun/Sep/Dec each Contract Year
Maintenance Requirement Check List
1 | Check for proper operating voltages and amp draws.
2 | Check controller, thermostat, and time clock settings; adjust as required.
3 | Check fan assembly and belts; replace belts annually
4 | Inspect and lubricate motors, bearings, linkages, louvers, dampers, fans, and other moving parts as required.
5 | Inspect and tighten electrical connections and components as required.
6 | Inspect all fan pulleys for wear, and adjust belt tensions as required.
7 | Inspect and clean condenser coils annually using environmentally friendly coil cleaner and water.
Note: AHA will provide a water source within 150 feet of furtherest piece of equipment.
8 | Inspect and clean, as required, all condensate hoses, drain pans, and "P" traps; if clogged, unblock.
9 | Inspect evaporator coils.
10 | Review all insulation; if damaged, replace.
11 | Replace gaskets as needed.
12 | Replace pleated air filter.
13 | Check compressor operation (operating pressures and oil levels).
14 | Check refrigerant lines and pressures for leaks; replace damaged refrigerant lines as needed.
15 | Check and adjust, as required, all safety controls and switches, including access panel limit switch;
replace limit switch if faulty

## AMP 400
AMP 400: CUMBERLAND GARDENS GYM
Location: | Rooftop | Manufacturer | Hastings HVAC, Inc.
Equipment: | Gas Hot Air Heat Only | Model No. | HRHVA 800V
|  | Inspection Dates | Fall
Maintenance Requirement Check List
1 | Clean flues
2 | Clean burners
3 | Clean air register, blower, and dampers
4 | Check pilot; adjust and clean
5 | Lubricate motor assembly
6 | Change filters
7 | Check belts and sheaves for alignment and belt tension; replace belts as needed
8 | Check thermostat operation
9 | Lubricate fan
10 | Review all valves for operation: if faulty replace
11 | Check all gas fittings for leaks
12 | Check blower: lubricate if needed
13 | Check operation of all limit and safety controls
14 | Assure power ventilator is operating correctly
15 | Check all electrical connections
16 | Inspect integrity of exterior duct
Location: | Rooftop | Manufacturer | Goodman Manufacturing, Inc.
Equipment: | Heat/AC Combo | Model No. | PGB030100-1REV-A
|  | Inspection Dates | Fall and Spring
Maintenance Requirement Check List
1 | Check blower motor: if needed, lubricate
2 | Check all valves for proper seal
3 | Clean all coils
4 | Furnish and replace air filter; wash permanent filters
5 | Check refrigerant charge; recharge up to 10 lbs
6 | Check compressor
7 | Check fan assembly
8 | Check condensation drain for blockage
9 | Check gas connections for leaks
10 | Clean burners
11 | Inspect fan motor blower: confirm clear from any obstruction
12 | Check seal on combustion compartment
13 | Check vents for obstruction
14 | Check heat exchanger and passage way: clean as required
15 | Check thermostat operation
16 | Check operation of all limits and safety controls
17 | Check vibration levels
18 | Check and record operating pressures
19 | Check and record voltage and amps of motors
AMP 400: CUMBERLAND GARDENS GYM
Location: | Rooftop | Manufacturer | Trane
Equipment: | Heat/AC Combo (#1, #2, and #3) | Model No. | YSC036A1RLA-H1000000A200-A
|  | Inspection Dates | Fall and Spring
Maintenance Requirement Check List
1 | Review fan belts: if frayed, replace
2 | Furnish and replace filters; wash permanent filters
3 | Check return air smoke detector
4 | Check the condensate overflow switch
5 | Clean all coils
6 | Clean refrigerant coils
7 | Check refrigerant charge; recharge up to 10 lbs
8 | Clean air register, blower, and dampers
9 | Clean and adjust ignition pilot assembly
10 | Check condensate lines
11 | Straighten out fins
12 | Check thermostat operation
13 | Check operation of all limit and safety controls
14 | Check all gas connections
15 | Check electrical connections
16 | Check and record operating pressures
17 | Check and record voltage and amps of motors
18 | Check integrity of exterior duct

## AMP 500
AMP 500: LITTLE LEHIGH
Locations: | Dwelling Units |  | Manufacturer | Ducane
| Building A: | 330 Lehigh Street and 340 Lehigh Street | Model No. | 95G1UH090CE16
| Building D: | 604 Lawrence Court and 618 Lawrence Court | Inspection Dates | Fall and Spring
| Building F: | 666 Lawrence Court and 680 Lawrence Court
| Building H: | 605 Lawrence Court and 619 Lawrence Court
| Building J: | 240 Lehigh Street and 254 Lehigh Street
Equipment: | Gas Furnace
Maintenance Requirement Check List
1 | Check fresh air intake grilles and louvers
2 | Inspect burners; brush and vacuum
3 | Check vent pipe
4 | Clean heat exchanger
5 | Check condensate trap
6 | Replace all filters
7 | Check air intake pipes
8 | Review blower
9 | Check all gas fittings
10 | Check all valves for proper operation
11 | Test all safety devices
Location: | Building G - Lawrence Court (Boiler #1 and #2) |  | Manufacturer | Weil McLain
| Building K - Lehigh Street (Boiler #1) |  | Model No. | Ultra 230
| Building K - Union Street (Boiler #2) |  | Inspection Dates | Fall
Equipment: | Gas Boilers
Maintenance Requirement Check List
1 | Check vent piping
2 | Check air piping
3 | Check relief valves
4 | Check condensate drain system
5 | Check pressure valves and gauges
6 | Check boiler piping for leaks
7 | Check all interior door gaskets: replace if bad seal is present
8 | Check ignition electrode: replace as needed
9 | Check expansion tank
10 | Check operation of all limit and safety controls
11 | Check and record amp draw on pump motors
12 | Lubricate all heat circulator motors and inspect couplings
13 | Inspect and clean breaching (from boiler to vertical riser)
14 | Clean heat exchanger
Location: | Building G - Lawrence Court |  | Manufacturer | Weil McLain
| Building K - Lehigh Street |  | Model No. | Aqua Plus 85
Equipment: | Indirect Water Heater |  | Inspection Dates | Fall
Maintenance Requirement Check List
1 | Check all valves
2 | Inspect pipes for signs of leaking
3 | Check water output temperature
4 | Inspect anode
5 | Drain tank and review interior
6 | Re-fill tank

## AMP 600
AMP 600: SCATTERED SITES
Location: | 412 N. Seventh Street | Manufacturer | Weil McLain
| 101 N. Third Street | Model No. | Ultra 399
| 145-149 Linden Street | Inspection Dates | Fall
Equipment: | Gas Hot Water Boiler
Maintenance Requirement Check List
1 | Check water piping
2 | Check vent piping
3 | Check air piping
4 | Check gas piping
5 | Check all valves for proper operation
6 | Check condensate drain for blockage
7 | Inspect refractory and boiler tubes
8 | Open, clean, and inspect low water cutoff controls
9 | Clean all combustion sights
10 | Clean and adjust ignition pilot assembly
11 | Check programmer operation
12 | Check operation of all limit and safety controls
13 | Check and record amp draw on pump motors
14 | Confirm water chemistry is within tolerance

## AMP 700
AMP 700: 700 BUILDING
Location: | Rooftop | Manufacturer | Technical Systems (RAE Division)
Equipment: | A/C Condenser | Model No. | 20AOLD18
|  | Inspection Dates | Fall and Spring
Maintenance Requirement Check List
1 | Flush tank
2 | Clean and lubricate fan assembly
3 | Clean surface debris and dirt in the unit
4 | Clean all coils
5 | Check refrigerant charge; recharge up to 10 lbs
6 | Check expansion valve operation
7 | Check operation of all limits and safety controls
8 | Check vibration levels
9 | Check and record operating pressures
10 | Measure and record amperage and temperature output
11 | Inspect the coil fins
12 | Inspect compressor and associated tubing for damage
Location: | Penthouse Mechanical Room | Manufacturer | Customaire
Equipment: | Heat/Air Handling | Model No. | DTH-110
|  | Inspection Dates | Fall and Spring
Maintenance Requirement Check List
1 | Check condensate line for blockage
2 | Check all gauges
3 | Check all valves
4 | Furnish and replace air filter; wash permanent filters
5 | Replace drive belt as needed
6 | Check refrigerant charge; recharge up to 10 lbs
7 | Check expansion valve operation
8 | Clean all coils
9 | Clean air register, blower, and dampers
10 | Check all gaskets are air tight
11 | Check all heating and cooling coils
12 | Check operation of all limits and safety controls
13 | Check vibration levels
14 | Check and record operating pressures
15 | Oil motor and fans
16 | Inspect integrity of exterior duct

## AMP 800
AMP 800: WALNUT MANOR
Location: | Mechanical Room | Manufacturer | Lochinvar
Equipment: | Domestic Hot Water Boiler (#1 and #2) | Model No. | AWN701PM
|  | Inspection Dates | Fall and Spring
Maintenance Requirement Check List
1 | Check pressure and temperature gauges
2 | Check vent and air piping
3 | Check condensate drain
4 | Check operator relief valves
5 | Check gas and water piping for leaks.
6 | Inspect interior
7 | Check control wiring
8 | Check condensate trap
9 | Check ignition and flame sensors
10 | Inspect and clean HEX and burner.
11 | Clean strainers.

## AMP 915
AMP 915: OVERLOOK PARK COMMUNITY BUILDING
Location: | Rooftop | Manufacturer | York
Equipment: | A/C Condenser (Zone 1 and Zone 5) | Model No. | CZB06011
|  | Inspection Dates | Spring
Maintenance Requirement Check List
1 | Clean dust or move objects away from the grates that supply air into each room
2 | Clean all coils
3 | Check the interior unit if dirty clean accordingly
4 | Check refrigerant charge; recharge up to 10 lbs
5 | Check expansion valve operation
6 | Check thermostat operation; set to cooling mode
7 | Check operation of all limits and safety controls
8 | Examine ducts
9 | Check vibration levels
10 | Replace air handler filter
11 | Check and record operating pressures
12 | Check and record voltage and amps of motors
13 | Make sure condensate line is clear to allow liquid runoff
Location: | Rooftop | Manufacturer | York
Equipment: | A/C Condenser (Zone 2 and Zone 3) | Model No. | CZB04811
|  | Inspection Dates | Spring
Maintenance Requirement Check List
1 | Clean dust or move objects away from the grates that supply air into each room
2 | Clean all coils
3 | Check the interior unit if dirty clean accordingly
4 | Check refrigerant charge; recharge up to 10 lbs
5 | Check expansion valve operation
6 | Check thermostat operation; set to cooling mode
7 | Check operation of all limits and safety controls
8 | Examine ducts
9 | Check vibration levels
10 | Replace air handler filter
11 | Check and record operating pressures
12 | Check and record voltage and amps of motors
13 | Make sure condensate line is clear to allow liquid runoff
Location: | Rooftop | Manufacturer | York
Equipment: | A/C Condenser (Zone 4) | Model No. | CZB03011
|  | Inspection Dates | Spring
Maintenance Requirement Check List
1 | Clean dust or move objects away from the grates that supply air into each room
2 | Clean all coils
3 | Check the interior unit if dirty clean accordingly
4 | Check refrigerant charge; recharge up to 10 lbs
5 | Check expansion valve operation
6 | Check thermostat operation; set to cooling mode
7 | Check operation of all limits and safety controls
8 | Examine ducts
9 | Check vibration levels
10 | Replace air handler filter
11 | Check and record operating pressures
12 | Check and record voltage and amps of motors
13 | Make sure condensate line is clear to allow liquid runoff
AMP 915: OVERLOOK PARK COMMUNITY BUILDING
Location: | Rooftop | Manufacturer | York
Equipment: | Heat and A/C Package (Zone 8 and Zone 10) | Model No. | ZJ048N10N1AAA1
|  | Inspection Dates | Fall and Spring
Maintenance Requirement Check List
1 | Check any vents for obstructions
2 | Check burner
3 | Clean flue passage
4 | Clean heating elements
5 | Furnish and replace air filter; wash permanent filters
6 | Replace drive belt as needed
7 | Clean blower assembly
8 | Clean condenser coils
9 | Check blower bearings
10 | Check refrigerant charge; recharge up to 10 lbs
11 | Check expansion valve operation
12 | Inspect gas valves for leakage
13 | Check thermostat operation
14 | Check operation of all limit and safety controls
15 | Check vibration levels
16 | Check and record operating pressures
17 | Check and record voltage and amps of mothers
18 | Inspect integrity of exterior duct
Location: | Rooftop | Manufacturer | York
Equipment: | Heat and A/C Package (Zone 9) | Model No. | ZJ060N10N1AAA1
|  | Inspection Dates | Fall and Spring
Maintenance Requirement Check List
1 | Check any vents for obstructions
2 | Check burner
3 | Clean flue passage
4 | Clean heating elements
5 | Furnish and replace air filter; wash permanent filters
6 | Replace drive belt as needed
7 | Clean blower assembly
8 | Clean condenser coils
9 | Check blower bearings
10 | Check refrigerant charge; recharge up to 10 lbs
11 | Check expansion valve operation
12 | Inspect gas valves for leakage
13 | Check thermostat operation
14 | Check operation of all limit and safety controls
15 | Check vibration levels
16 | Check and record operating pressures
17 | Check and record voltage and amps of mothers
18 | Inspect integrity of exterior duct

## NSA
NSA: MAJESTIC BUILDING AND A/B BUILDING
Location: | Basement - Majestic Building | Manufacturer | Weil McLain
Equipment: | Gas Hot Water Boiler | Model No. | LGB-9
|  | Inspection Dates | Fall
Maintenance Requirement Check List
1 | Open fireside; brush, vacuum, reseal
2 | Inspect and clean breaching (from boiler to vertical riser)
3 | Check all valves
4 | Check expansion tanks
5 | Check air vents
6 | Check all gauges
7 | Check gas valves
8 | Check water temperature limit switch
9 | Check transformer
10 | Check spill switch
11 | Review air pressure switch
12 | Check and record amp draw on pump motors
13 | Check pilot burner
14 | Check vent termination and air intake screens
15 | Check condensate drain system
Location: | Basement - A/B Building | Manufacturer | Weil McLain
Equipment: | Gas Hot Water Boiler | Model No. | PFG-7-P1N
|  | Inspection Dates | Fall
Maintenance Requirement Check List
1 | Open fireside; brush, vacuum, reseal
2 | Check all valves
3 | Check expansion tanks
4 | Check air vents
5 | Check all gauges
6 | Check gas valves
7 | Check water temperature limit switch
8 | Check transformer
9 | Check spill switch
10 | Review air pressure switch
11 | Check and record amp draw on pump motors
12 | Check pilot burner
13 | Check vent termination and air intake screens
14 | Check condensate drain system
15 | Inspect insulation